First: Project Input Parameters

| Parameter | Value | Unit |
| --- | --- | --- |
| Capacity_KG | 480 | kg |
| Car_Weight_KG | 500 | kg |
| CW_Weight_KG | 740 | kg |
| Rope_Diameter_MM | 11 | mm |
| Number_of_Ropes | 4 | count |
| Suspension_Ratio | 2 | :1 |
| Car_Width_M | 1.1 | m |
| Car_Depth_M | 2.1 | m |
| Guide_Shoe_Distance_M | 1.2 | m |
| Machine_Weight_KG | 250 | kg |
| Compens_Weight_KG | 600 | kg |
| W_Factor_1 | 950 |  |
| W_Factor_2 | 850 |  |
| W_Divisor | 1800 |  |
| P_Factor_1 | 400 |  |
| P_Factor_2 | 200 |  |
| P_Divisor | 600 |  |
| Parachute_Deceleration_M_S2 | 1.962 | m/s² |
| Parachute_Load_Multiplier | 10 | N/kg |
| Brake_Ratio | 1 |  |
| Gravity_G | 9.81 | m/s² |
| Buffer_Factor | 4 |  |

Second: Ropes Static Tension Calculations

A) Static tension in each car suspension rope

T1 = (Capacity + Car + Compens) × g / 8

= (480 + 500 + 600) × 9.81 / (2 × 4) = 1937.475 N

B) Static tension in each C.W. suspension rope

Tcw = CW × g / 8 = 740 × 9.81 / 8 = 907.425 N

Third: Calculating the forces of irregular load distribution inside the car

A) The Force FF1 (In the direction of the car guide rail axis)

FF1 = Capacity x 10 x Car Width / (4 x Vertical Guide Shoe Distance).

FF1 = 480 X 10 X 1.10  / (4 X 1.2)  =  1100 N.

FF1 (design) = 1100 × 2 = 2200 N.

FF1 ≈ 224.34 kgf

B) The Force FF2 (Perpendicular to the car guide rail axis).

FF2 = Capacity x 10 x Car Depth / (8 x Vertical Guide Shoe Distance).

FF2 = 480 X 10 X 2.10  / ( 8 X 1.20  ) =   1050 N.

FF2 (design) = 1050 × 2 = 2100 N.

FF2 ≈ 214.14 kgf.

Fourth: Bedplate Load Distribution Calculations

W_Total = (480 + 500 + 740 + 600 + 250) × 9.81 = 25211.70 N

W1 = W_Total × 950/1800 = 13306.175 N; W2 = W_Total × 850/1800 = 11905.525 N

| ΣP = W_Total |  |  |  |
| --- | --- | --- | --- |
| P1 = W1×400/600 ≈ 8870.78 N ≈ 904.57 kgf | P2 = W2×400/600 ≈ 7937.02 N ≈ 809.35 kgf | P3 = W2×200/600 ≈ 3968.51 N ≈ 404.68 kgf | P4 = W1×200/600 ≈ 4435.39 N ≈ 452.28 kgf |

Fifth: Calculating the safety gear braking load on each car guide rail (Progressive Safety Gear).

P5 = (Capacity + Car + Compens) × 10 N/kg

= (480 + 500 + 600) × 10 = 15800 N ≈ 1611.15 kgf [Per Guide Rail]

Sixth: Loads on the pit supports below the car buffer | P6 (BUFFERS)

P6 = (Capacity + Car + Compens) × max(40, Buffer × g) N/kg

= (480 + 500 + 600) × max(40, 4 × 9.81) = 63200 N ≈ 6444.61 kgf [One Buffer]

Seventh: Pit support loads below the C.W. buffer | P7 (BUFFERS)

P7 = CW × max(40, Buffer × g) N/kg

= 740 × max(40, 4 × 9.81) = 29600 N ≈ 3018.36 kgf [One Buffer]

CODE - STANDARDS :

Diameter of ropes: The nominal diameter of ropes must not be less than 8 mm.

Tensile strength of rope wires: The tensile strength must be at least 1300 N/mm² and not more than 1800 N/mm².

Safety factor for ropes: Minimum breaking load divided by maximum rope tension must be at least 12 and not less than the value calculated under EN 81-50.

Number of ropes: At least 3 independent suspension ropes are required.

Rope data: Rope characteristics (construction, extension, ovality and flexibility) must comply with EN 12385-5.

The pitch diameter of traction sheaves and pulleys must be at least 40 times the nominal suspension rope diameter.

Rope terminations must withstand at least 80% of the minimum breaking load of the rope.

Rope traction: The car must not be raised by the machine when the counterweight rests on its buffers.